SECTION 26 12 16

Dry-Type Cast Resin, Medium Voltage Transformers

Typical Specification

Phone:  1-888-798-8882 (Canada)

1-800-537-0500 (US)

E-mail: sales@hammondpowersolutions.com

www.hammondpowersolutions.com

SECTION 26 12 16

Dry-Type Cast Resin, Medium Voltage Transformers

- GENERAL

  - SCOPE

    - This section defines the requirements for the design, manufacture and testing of dry-type cast resin, enclosed and ventilated medium voltage (power) transformers as indicated herein and on the project drawings.

    - Transformers shall be designed, constructed and rated in accordance with UL, CSA, NEMA and IEEE/ANSI standards (where applicable).

C	Transformers shall be designed, constructed and rated (where applicable) in accordance with U.S. Department of Energy, Energy Conservation Program for Commercial Equipment; Distribution Transformers Energy Conservation Standards.

      - DOE 2016 – DOE 10 CFR Part 431 Efficiency Standards; published in the Federal Register on April 18, 2013

      - NRCan (Natural Resources Canada), Energy Efficiency Act SOR/2018-201, amendment 14 effective April 30th, 2019.

      - Ontario Green Energy Act, revised by ON Reg.404-12 effective January 1st, 2018.

  - RELATED DOCUMENTS

    - Drawing and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

  - REFERENCES

    - IEEE C57.12.01 - General Requirements for Distribution, Power and Regulating Transformers

    - ANSI C57.12.28 - Switchgear and Transformers, Pad-Mounted Equipment - Enclosure Integrity

    - ANSI C57.12.50 - Requirements for Ventilated Dry-Type Distribution Transformers, 1-500 kVA Single-Phase and 15-500 kVA Three-Phase, with High Voltage 601-34,500 Volts, Low Voltage 120-600 Volts

    - ANSI C57.12.51 - Requirements for Ventilated Dry-Type Power Transformers, 501 kVA and Larger Three-Phase, with High Voltage 601-34,500 Volts, Low Voltage 208Y/120-4160 Volts

    - ANSI C57.12.55 - Conformance Standard for Transformers - Dry-Type Transformers Used in Unit Installations, Including Unit Substations

    - IEEE C57.12.56 - Standard Test Procedure for Thermal Evaluation of Insulation Systems for Ventilated Dry-Type Power and Distribution Transformers

    - IEEE C57.12.58 - Guide for Conducting a Transient Voltage Analysis of a Dry-Type Transformer Coil

    - IEEE C57.12.59 - Guide for Dry-Type Transformer Through-Fault Current Duration

    - IEEE C57.12.70 - Terminal Markings and Connections for Distribution and Power Transformers

    - IEEE C57.12.80 - Standard Terminology for Power and Distribution Transformers

    - IEEE C57.12.91 Standard Test Code for Dry-Type Distribution and Power Transformers,

    - IEEE C57.94 - Recommended Practice for Installation, Application, Operation, and Maintenance of Dry-Type General Purpose Distribution and Power Transformers

    - IEEE C57.96 - Guide for Loading Dry-Type Distribution and Power Transformers (ANSI).

    - IEEE C57.105 - Guide for Application of Transformer Connections in Three-Phase Distribution Systems

    - C57.110 for non-linear loads and C57.18.10 for rectifier duty if specified

    - IEEE C57.124 - Recommended Practice for the Detection of Partial Discharges and the Measurement of Apparent Charge in Dry-Type Transformers

    - CSA-C88 - Power Transformers and Reactors

    - UL 1562 Transformers, Distribution, Dry-Type - Over 600 Volts

    - DOE 2016 – DOE 10 CFR Part 431 Efficiency Standards; published in the Federal Register on April 18, 2013

    - Natural Resources Canada, Canada Energy Efficiency Act, Energy Efficiency Regulations, SOR/2018-201 amendment 14 effective April 30th, 2019

    - Ontario Green Energy Act revised by ON Reg.404-12 schedule 6 effective January 1st, 2018.

    - Ontario Energy Efficiency Regulations 404/12 (2018)

    - NEMA 210 - Secondary Unit Substations

    - NEMA TR-27 - Commercial, Institutional and Industrial Dry-Type Transformers

  - SUBMITALS

    - Customer name. Customer location and customer order number shall identify all transmittals.

    - Submit shop drawing and product data for approval and final documentation in the quantities listed according to the Conditions of the contract.

    - Product related details to be provided:

      - KVA rating

      - HV (Primary) and LV (Secondary) voltage

      - HV (Primary) and LV (Secondary) Basic Impulse Level (BIL)

      - HV (Primary) voltage taps

      - Insulation temperature class and temperature rise

      - Unit dimensions & weight

      - Impedance

      - Conductor material

      - Efficiency (where applicable) per NRCan (Natural Resources Canada) Regulations (SOR/2018-201) and/or Ontario 404/12 (2018) and/or US Regulations (DOE 10 CFR Part 431)

      - Bus connection detail (if applicable)

      - Interface details for close-coupled equipment (if applicable)

  - QUALITY ASSURANCE & TESTING

    - The manufacturer shall have a well-documented quality assurance program, which includes procedures for all activities in order entry, design, material procurement, manufacturing processes, testing and logistics.

    - The manufacturer shall have specialized in the design, manufacture and assembly of dry-type distribution transformers for a minimum of 25 years in North America.

    - The transformer shall be manufactured by a company, which is certified to ISO 9001, for design and manufacture of dry-type transformers.

    - The test floor shall have documented calibration program. All equipment shall receive regular calibrations. Calibration standards shall be traceable to National Bureau of Standards.  Measured values of electric power, voltage, current, resistance and temperatures are used in the calculations of reported data.  To ensure sufficient accuracy in the measured and calculated data the test system accuracy requirements listed in ANSI C57.12.01 Table 3 shall be met as a minimum.

    - Production tests: each unit according to:

      - CSA C9 & C22.2 No. 47

      - UL 1562

      - DOE 10 CFR Part 431 sub part K

    - Test each model design and submit report on request

    - Standard production tests to include:

      - Polarity

      - Voltage Ratio

      - Resistance of coils *

      - Partial Discharge

      - Power frequency voltage-withstand tests on each winding

      - Induced voltage test

      - No load loss and excitation current

      - Impedance test and load loss *

* - Typically not performed on units ≤ 500 kVA

    - Additional type test should be made available on request include:

      - Temperature rise test

      - BIL – basic impulse insulation level test

      - Sound level test

      - Insulation resistance test

      - Short circuit test

- PRODUCTS

  - ManufacturerS:

    - Hammond Power Solutions Inc.

Substitutions are permitted, subject to meeting all requirements of this specification and also having written approval by Engineering prior to bid closing.

  - General construction:

    - Transformer core shall be manufactured from quality non-aging, cold rolled, grain-oriented silicon steel laminations. Cores are to be precisely cut to close tolerances to eliminate burrs and improve performance.  Design configuration is to be step-lap, fully mitered construction for optimum energy efficiency and low noise level. Cores are to be carefully assembled and rigidly held secure with structural steel clamps to minimize gaps.  Core is to be protected from corrosion by painting after assembly.  Core dipping is not acceptable as the sole means of protection.

    - Where applicable, high and low voltage windings shall each be separately cast as one rigid tubular coil, and arranged coaxially.  Each cast coil shall use a mineral-filled epoxy reinforced with fiberglass mat, and cast to provide complete, void-free resin impregnation throughout the entire insulation system. The coil supports shall maintain constant pressure during thermal expansion and contraction of the coils.

    - HV (Primary) and LV (Secondary) terminations to be mounted on separate insulated supports.

  - Voltage and kVA Requirements:

    - HV (Primary) Voltage: [34500][25000][13800][12470][6900][4160][2400][other]

    - HV (Primary) Connection:  [Delta] [Wye]

    - HV (Primary) Voltage BIL Rating: [20][30][45][60][95][110][125][150][other]

    - LV (Secondary) Voltage:  [120/208][277/480][347/600][2400][4160][other]

    - LV (Secondary) Connection:  [Wye] [Delta]

    - LV (Secondary) Voltage BIL Rating: [10][20][30][45][other]

    - kVA rating:  [500][750][1000][1250][1500][2000][2500][3000][other]

    - System Frequency:  60 [50] [other] Hertz

  - design requirements:

    - Three-phase, common core construction

    - Conductor material shall be [Copper] [Aluminum]

    - Cooling shall be [Air cooled] [Fan Cooled]

    - Insulation system temperature class [185/180°C] 155/150°C] [other]

    - Average winding rise by resistance shall not exceed [80°C] [115°C] [other]

    - The transformer(s) shall be capable of carrying 100% of nameplate kVA rating in a 40 °C maximum, 30 °C average ambient as defined by CSA C9-02 (IEEE C57.12.01)

    - Standard impedance at 60Hz: [5.5% to 8%] [other]

    - Name Plate Rating:  Linear load, 60Hz

    - Efficiencies: (where applicable)

      - Meets and exceeds NRCan (Natural Resources Canada), Energy Efficiency Act SOR/2018-201, amendment 14 effective April 30th, 2019.

      - Meets and exceeds Ontario Green Energy Act, revised by ON Reg.404-12 effective January 1st, 2018.

      - Meets or exceeds US Energy Efficiency Regulations (DOE 10 CFR Part 431) published in the Federal Register on April 18, 2013 effective as of January 1st, 2016.

      - Efficiencies at 50% of rated load on units having a primary voltage BIL rating greater than 1.2kV

      - Refer to the DOE 10 CFR Part 431 Energy Efficiency Standards and/or NRCan 2019 for product exemption criteria.

    - Four high voltage taps shall be provided; two at 2.5% FCAN and two at 2.5% FCBN. Off circuit, tap selection shall be by tap links.

    - Coil Impregnation:

      - HV (Primary) – cast epoxy resin

      - LV (Secondary) – [cast epoxy resin] [vacuum pressure impregnated (VPI) polyester resin]

    - Sound level to meet [CSA C9-02] [other]

    - Enclosure:  [ventilated NEMA 1][NEMA 3R][NEMA 3R c/w filters][totally enclosed] [other].

    - Enclosure Finish:  [ANSI 61 Grey] [ANSI 61 Grey suitable for CSA C22.2.94.2 (UL 50) outdoor applications] [other].

    - Anti-vibration pads/isolators shall be used between the transformer core and coil and the enclosure.

    - Agency Approval [CSA][UL] [other]

  - Optional equipment:

The following optional equipment shall be provided, as defined within the project documentation:

- Fan mounted provisions only for future forced air-cooling.

- Forced air-cooling; 120V Power will be [supplied] [not supplied]

- Forced air cooling with increased full-load kVA capacity [33%]

- Taps shall be FCAN XX%., FCBN XX%, and RCBN XX%.

- Lightning arrestors rated for system voltage [Station class] [Intermediate class] [Distribution class]

- A grounding resistor shall be provided [details per project documentation]

- A Neutral Ground Monitor shall be provided [details per project documentation]

- Thermometers: [dial 2 contacts][dial 3 contacts][4-20mA o/p thermocouple input][other]

- Trip Thermostat (1 per phase): [N.O. 150°C][N.C. 150°C][other]

- Alarm Thermostat (1 per phase): [N.O. 130°C][N.C. 130°C][other]

- Nameplate shall be [Aluminum][Stainless Steel]

- A key interlock to prevent unauthorized access shall be provided [Kirk key interlock] [Kirk key interlock with indicating signal light that indicates doors are open]

- Current transformers shall be provided [details per project documentation]

- Potential transformer shall be provided [details per project documentation]

- An electrostatic shield shall be provided

- Transformer shall be designed to handle current harmonics [K4] [K13] [K20] [other]

- A strip heater powered from separate source shall be provided [details per project documentation]

- Design shall meet seismic requirements for the  International Building Code (IBC) 2018, and the American Society of Civil Engineers  ASCE 7-16 specifications, with the following seismic design parameters defined:

- Spectral acceleration:         Sds

- Importance Factor:              Ip

- Attachment/height ratio:      z/h

- Additional anti-vibration options: [Super W Pads][Spring Isolators][Springs & Snubbers]

- Low Sound Level: [-3 dB][ -5 dB][-8 dB][other]

- Surge Protection Device shall be provided [details per project documentation]

- Rolling and Skidding Base: [2 directions] [4 directions]

- Provision for Lifting and Jacking

##### EXECUTION

  - DELIVERY, STORAGE AND HANDLING

    - Equipment shall be handled and stored in accordance with manufacturer’s instructions. One (1) copy of these instructions shall be included with the equipment at time of shipment.

    - Protect equipment from potential damage from weather and construction operations. Store so condensation will not form on or in the transformer housing and, if necessary, apply temporary heat to obtain suitable service conditions.

    - Handle transformer using proper equipment for lifting and handling, use when necessary lifting eye and/or brackets provided for that purpose.

  - Installation

    - The installing contractor shall install the Dry-Type Medium Voltage (Power) Transformer per the manufacturer's recommended installation practices as found in the installation, operation, and maintenance manual and comply with all applicable codes.

    - Make sure that the transformer is level.

    - The transformer shall be mounted on a concrete pad unless otherwise indicated.

    - Check for damage and loose connections.

    - Mount transformer on suitable isolation pad to minimize vibrations.

    - Install seismic restraint where indicated on the drawing.

    - Coordinate all work in this section with all work of other sections.

    - Take Infrared Picture to verify connections accuracy or deficiencies.

    - Prior to energizing transformer, verify secondary voltages and if necessary adjust secondary taps.

    - Report on the Commissioning of the transformer shall include:

      - Primary & Secondary Voltages

      - Primary & secondary THDi & THDv